## Slide 1: Cimberio Energy Valve
Reserved and confidential
CSxxxSC
25/05/2022

## Slide 2: General features - This is it
Reserved and condifential
Energy meter with integrated control valve
Building automation connectivity (BMS): Modbus, BacNet, MQTT
Measurement and control of:
  Flow
  Differential ΔT(T1-T2)
  Flow temperature (T1)
  Return temperature (T2)
  Power
  Valve position
  MID certification compatible (Flow and Energy)
Embedded electronic control unit

## Slide 3: Concept – Quick look
Reserved and condifential
Energy valve,
main components:
Electromagnetic flow meter
Temperature sensors
Electronic control unit
Regulating valve
Valve Actuator

## Slide 4: Electromagnetic flow meter
Reserved and condifential
Features:
High accuracy flow measurement;
Glycols in the water do not affect the flow measurement;
Less prone to problem in case of air bubble in the network

## Slide 5: Electronic control unit
Reserved and condifential
Features:
Building automation connectivity
Enersem Cloud compatible
BMS compatible
Modbus and other protocols
Heating and cooling energy counters
Accurate flow measurement
T1, T2, ΔT measurement
Power and Energy measurement
Ethernet port
Serial port RS485
USB port (service)
Display (optional)

## Slide 6: Temperature sensors
Reserved and condifential
Features:
Connection: screw connection
Paired calibration
Type: Pt500/Pt1000;
N° wires: two-wire
Temperature range: 0 to 180 °C
Maximum pressure: PN 25
Protection type: IP65

## Slide 7: Valve Actuator
Reserved and condifential
Features:
Voltage: 24V-50/60 Hz AC/DC;
Rotation angle: 90°;
Opening/closing time: 60’’
Control: proportional
Protection degree: IP54
Operating torque: 10 Nm
Position: measure of valve opening degree;
Position indicator: knob on cover
Manual operation: yes

## Slide 8: Valve body and regulating valve
Reserved and condifential
Features:
Body made of dezincification resistant brass
Size range: DN15÷DN50
PN25
Thermodynamic parameters measurement
Equipercent characterized ball valve

## Slide 9: Comparison
CIMBERIO | BELIMO | TOUR ANDERSON | SIEMENS
Electromagnetic | Ultrasonic | Ultrasonic | Ultrasonic
Compact Single piece | No single piece | Single piece | No single piece
½» - 2» | ½» - 2» | 1»1/4 – 2» | ½» - 2»
MODBUS BACNET MQTT | MODBUS BACNET | MODBUS BACNET MQTT | MODBUS BACNET
Characterized ball valve | Characterized ball valve | Globe | Characterized ball valve

## Slide 10: Thank you for your attention

## Slide 11: Block diagram – inside look
Reserved and condifential
Flow meter
Regulating valve
Electrical actuator
Flow
Flow
Electronic control unit
T2 temperature sensor
T1 temperature sensor
T1 = flow temperature sensor
T2 = return temperature sensor
Flow
Heat exchangers
Heat generator
Flow